## PythonCode
Python code to compute performance metrics of heat pumps vs refrigerant, source and drain temperatures and condenser state (temperature for NH3, pressure for CO2)
"""
Computes performance metrics for a heat pump using CoolProp.
The performance metrics are computed relative to the compression volume flow rate (swallowing ability).
The performance metrics are:
- Work: Compression work.
- qEvap: Latent heat absorbed.
- qOut: Heat output.
- Yield: Heat output normed by yield at source temperature of 4.0°C and drain temperature of 40.0°C.
- COP: Coefficient of performance.
CoolProp is a C++ library that implements the thermophysical properties of fluids.
See: http://www.coolprop.org/index.html
conda install -c conda-forge::coolprop
pip install pyfluids
Author: Mogens Bech Laursen
2025 March 03
"""
import os
from weakref import ref
import numpy as np
import pandas as pd
# from pyfluids import Fluid, FluidsList
from CoolProp.CoolProp import PropsSI
import matplotlib.pyplot as plt
import xlwings as xw
from sklearn.linear_model import LinearRegression
from sklearn.preprocessing import PolynomialFeatures
os.chdir(os.path.join(os.getcwd(), 'CoolProp'))
print(f'curdir: {os.getcwd()}')
# Reference state for CoolProp shall be set to h=200 kJ/kg and s=1 kJ/kgK for saturated liquid at 0°C. (IIR).
global TKelvin
TKelvin = 273.15
refrigerants = ['NH3', 'CO2']
hOfzRef = {refrig: PropsSI('H', 'T', 0.0+TKelvin, 'Q', 0, refrig) - 200E3 for refrig in refrigerants}
sOfzRef = {refrig: PropsSI('S', 'T', 0.0+TKelvin, 'Q', 0, 'NH3') - 1E3 for refrig in refrigerants}
print(f'hOfz: {hOfzRef}')
print(f'sOfz: {sOfzRef}')
# def is_file_synchronized(file_path: str) -> bool:
# """
# Check if the file is synchronized to the local machine using Dropbox.
# """
# dbx = dropbox.Dropbox('YOUR_ACCESS_TOKEN')
# try:
# metadata = dbx.files_get_metadata(file_path)
# return metadata.server_modified is not None
# except dropbox.exceptions.ApiError as e:
# print(f"API error: {e}")
# return False
def calc(TsourceC: float, TdrainC: float, pCond: float, refrig: str) -> list[float]:
""" \
Calculate the performance metrics of a heat pump:
- TsourceC: Source temperature in Celsius.
- TdrainC: Drain temperature in Celsius.
- TcondC: Condenser temperature in Celsius.
- refrig: Refrigerant name.
Returns:
- Tsource, Tdrain, Tcond (input temperatures)
- pA: Pressure at source temperature and quality 0 (liquid).
- hA: Enthalpy at source temperature and quality 0 (liquid).
- hB: Enthalpy at source temperature and quality 1 (saturated vapour).
- hC: Enthalpy at condenser pressure and entropy at B.
- hD: Enthalpy at drain temperature and quality 0 (liquid).
- sB: Entropy at source temperature and quality 1 (saturated vapour).
- work: Compression work.
- qEvap: Latent heat absorbed.
- qOut: Heat output.
- yield: Heat output.
- COP: Coefficient of performance.
The performance metrics are computed relative to the compression volume flow rate (swallowing ability).
"""
Tsource = TsourceC + TKelvin
Tdrain = TdrainC + TKelvin
pA = PropsSI('P', 'T', Tsource, 'Q', 0, refrig) # Pressure at source temperature and quality 0 (liquid).
hD = PropsSI('H', 'T', Tdrain, 'P', pCond, refrig) # Enthalpy at drain temperature and quality 0 (liquid).
hA = hD
hB = PropsSI('H', 'T', Tsource, 'Q', 1, refrig) # Enthalpy at source temperature and quality 1 (saturated vapour).
dhAB = hB - hA
densB = PropsSI('D', 'T', Tsource, 'Q', 1, refrig) # Density at source temperature and quality 1 (saturated vapour).
sB = PropsSI('S', 'T', Tsource, 'Q', 1, refrig) # Entropy at source temperature and quality 1 (saturated vapour).
hC = PropsSI('H', 'P', pCond, 'S', sB, refrig) # Enthalpy at condenser pressure and entropy at B.
# Performance metrics relative to the compression volume flow rate (swallowing ability).
work = densB * (hC - hB) # Compression work.
qEvap = densB * dhAB # Latent heat absorbed.
y = work + qEvap # Heat output.
COP = y / work # Coefficient of performance.
hOfz = hOfzRef[refrig]
sOfz = sOfzRef[refrig]
result = {'Tsource': TsourceC, 'Tdrain': TdrainC, 'pCond': pCond, \
'pA': pA, 'hA': hA-hOfz, 'hB': hB-hOfz, 'hC': hC-hOfz, 'hD': hD-hOfz, 'sB': sB-sOfz, \
'Work': work, 'qEvap': qEvap, 'qOut': work+qEvap, 'Yield': y, 'COP': COP}
return result
def performPolyFit(degree: int, df: pd.DataFrame, featureNames: list[str]) -> tuple[float, np.ndarray, np.ndarray, LinearRegression]:
""" \
Perform polynomial regression on the yield data.
- degree: Degree of the polynomial regression. Defaults to 2.
- dfResults: DataFrame with the results.
- featureNames: List of feature names e.g. ['Tsource', 'Tdrain']
Returns:
- score: R^2 score.
- intercept: Intercept of the polynomial regression.
- coef: Coefficients of the polynomial regression for each polynomial combination of features.
"""
# TODO Include Tcond / pCond as independent variable.
# Reshape the data as a 2D array of independent variable values.
X = df[featureNames].values
y = df['YieldNormed'].values
# Perform polynomial regression.
poly = PolynomialFeatures(degree=degree)
X_poly = poly.fit_transform(X) # Returns a Vandermonde matrix with the polynomial combinations of the features, one row per observation.
model = LinearRegression()
linReg = model.fit(X_poly, y)
# Test the polynomial regression.
predictedYield = model.predict(X_poly)
# Get the attributes of the model.
coef = model.coef_
intercept = model.intercept_
score = model.score(X_poly, y)
print(f'coef: {coef}, intercept: {intercept}, score: {score}')
return (score, intercept, coef, model)
TcondsC = [60.0, 70.0, 80.0] # Forward condenser temperature in Celsius for NH3.
pConds = [90E5, 100E5, 110E5] # Forward condenser pressure in Pa for CO2.
TsourceRefC = 4.0 # Independent of refrigerant, tied to source inlet temperature.
TdrainRefC = 40.0 # Independent of refrigerant, tied to district heating return temperature.
results: dict[str, pd.DataFrame] = {} # Key is combination of refrigerant and condenser state (temp. or pressure).
# # DEBUG
# refrigerants = ['NH3']
# TcondsC = [60.0]
# pConds = [90E5]
for refrig in refrigerants:
for iCond in range(len(TcondsC)): # Loops either TcondsC or Pconds
dfResults = pd.DataFrame(columns=['Tsource', 'Tdrain', 'pCond', 'pA', 'hA', 'hB', 'hC', 'hD', 'sB', 'Work', 'qEvap', 'qOut', 'Yield', 'COP'])
TdrainsC = np.arange(30.0, 50.0+0.5, 2.0)
TsourcesC = np.arange(00.0, 20.0+0.5, 2.0)
if refrig == 'NH3':
TcondC = TcondsC[iCond] # Forward condenser temperature in Celsius.
Tcond = TcondC + TKelvin # Underkritisk NH3.
title = f'{refrig} at Tcond={int(TcondC)}°C'
pCond = PropsSI('P', 'T', Tcond, 'Q', 0, refrig) # Condensation pressure at condensor source temperature and quality 0 (liquid).
elif refrig == 'CO2':
pCond = pConds[iCond] # Forward condenser pressure in bar for CO2.
title = f'{refrig} at pCond={int(pCond/1E5)} bar'
try:
for TsourceC in TsourcesC:
for TdrainC in TdrainsC:
dfResults.loc[len(dfResults), :] = calc(TsourceC, TdrainC, pCond, refrig)
except Exception as e:
print(f'Error: {e}')
print(f'TsourceC: {TsourceC}, TdrainC: {TdrainC}, pCond: {pCond}, refrig: {refrig}')
# Compute the performance metrics at reference state and normalize the yield factor.
resultsRef = calc(TsourceRefC, TdrainRefC, pCond, refrig)
dfResults['YieldNormed'] = dfResults['Yield'] / resultsRef['Yield']
# Create pivot tables for the performance metrics.
dfYield = dfResults.pivot(index='Tsource', columns='Tdrain', values='YieldNormed')
dfCOP = dfResults.pivot(index='Tsource', columns='Tdrain', values='COP')
results[title] = (dfResults, dfYield, dfCOP)
# Perform polynomial regression on the yield data.
# See: https://www.kaggle.com/code/peymankarimi74/simple-multiple-and-polynomial-regression
# See: https://saturncloud.io/blog/multivariate-polynomial-regression-with-python/
regrs: dict[str, tuple[float, np.ndarray, np.ndarray, LinearRegression]] = {} # Key is title, Value is tuple of score, intercept, coef, model.
degree = 2
for title in results.keys():
dfResults, dfYield, dfCOP = results[title] # Unpacking.
score, intercept, coef, model = performPolyFit(degree=degree, df=dfResults, featureNames=['Tsource', 'Tdrain'])
print(f'{title}: score: {score}, coef: {coef}, intercept: {intercept}')
regrs[title] = (score, intercept, coef, model)
pass
# Write the results to Excel files.
xlApp = xw.App(visible=True, add_book=False)
wb = xlApp.books.open('HP performance metrics TEMPLATE.xlsx')
for title in results.keys():
dfResults, dfYield, dfCOP = results[title] # Unpacking thermodynamic results.
score, intercept, coef, model = regrs[title] # Unpacking regression results.
sh = wb.sheets['Refrig'].copy(name=title)
pCond = dfResults['pCond'].iloc[0]
sh.range('B1').value = title[:3]
sh.range('B2').value = TsourceRefC
sh.range('B3').value = TdrainRefC
sh.range('B4').value = pCond / 1E5
sh.range('B5').value = degree
sh.range('B6').value = score
sh.range('B7').value = intercept # Special handling of the intercept.
sh.range('C7').value = coef[1:]
sh.range('A10').value = dfYield
sh.range('A30').value = dfCOP
sh.range('A50').value = dfResults
wb.save(f'HP performance metrics - {degree=}.xlsx')
wb.close()
xlApp.quit()

## Refrig
Refrigerant | NH3 |  |  | Relativ VP-ydelse vs. dræn- og kildetemp. for NH3 @ Pcond 33 bar
TsourceRef | 4 | °C | [12 empty] | Beregning af YieldFactor
TdrainRef | 40 | °C |  | REF | 40 | 1 | [8 empty] | Tsource | 4
Pcond | 33.12 | bar | [12 empty] | Tdrain | 40
Degree | 3 | [13 empty] | YieldFactor | 1
Score | 1
Coef. | 1.0093 | 0.03197 | -0.0031532 | 0.00041091 | -9.6302e-05 | 2.1034e-06 | 2.1465e-06 | -1.9714e-06 | -1.8954e-07 | -5.009e-08
Koefficienter er listet i rækkefølgen: { 1, x, y, x**2, xy, y**2, x**3, x**2 y, x y**2, y**3, …}
Yield rel. to Ref. | Tsource\Tdrain
| 30 | 32 | 34 | 36 | 38 | 40 | 42 | 44 | 46 | 48 | 50
0 | 0.91438 | 0.90827 | 0.90214 | 0.89599 | 0.88981 | 0.8836 | 0.87736 | 0.87108 | 0.86478 | 0.85844 | 0.85206
2 | 0.97344 | 0.9669 | 0.96032 | 0.95372 | 0.94708 | 0.94042 | 0.93372 | 0.92699 | 0.92023 | 0.91342 | 0.90658
4 | 1.0354 | 1.0284 | 1.0213 | 1.0143 | 1.0071 | 1 | 0.99282 | 0.98561 | 0.97836 | 0.97106 | 0.96373
6 | 1.1003 | 1.0928 | 1.0853 | 1.0777 | 1.0701 | 1.0624 | 1.0547 | 1.047 | 1.0393 | 1.0314 | 1.0236
8 | 1.1684 | 1.1603 | 1.1522 | 1.1441 | 1.136 | 1.1278 | 1.1196 | 1.1113 | 1.103 | 1.0947 | 1.0863
10 | 1.2396 | 1.231 | 1.2223 | 1.2137 | 1.205 | 1.1962 | 1.1874 | 1.1786 | 1.1697 | 1.1608 | 1.1518
12 | 1.3141 | 1.3049 | 1.2957 | 1.2864 | 1.2771 | 1.2678 | 1.2584 | 1.249 | 1.2395 | 1.23 | 1.2204
14 | 1.392 | 1.3822 | 1.3723 | 1.3625 | 1.3526 | 1.3426 | 1.3326 | 1.3225 | 1.3124 | 1.3022 | 1.292
16 | 1.4734 | 1.4629 | 1.4525 | 1.4419 | 1.4314 | 1.4208 | 1.4101 | 1.3994 | 1.3886 | 1.3777 | 1.3668
18 | 1.5584 | 1.5473 | 1.5361 | 1.5249 | 1.5137 | 1.5024 | 1.491 | 1.4796 | 1.4681 | 1.4566 | 1.4449
20 | 1.6472 | 1.6354 | 1.6235 | 1.6116 | 1.5996 | 1.5876 | 1.5755 | 1.5633 | 1.5511 | 1.5388 | 1.5264
COP Carnot | Tsource\Tdrain
Tsource | 30 | 32 | 34 | 36 | 38 | 40 | 42 | 44 | 46 | 48 | 50
0 | 4.4756 | 4.3463 | 4.2103 | 4.0664 | 3.9124 | 3.7457 | 3.5631 | 3.3614 | 3.1379 | 2.8928 | 2.6349
2 | 4.6731 | 4.5354 | 4.3907 | 4.2374 | 4.0734 | 3.8959 | 3.7014 | 3.4866 | 3.2486 | 2.9875 | 2.7129
4 | 4.8879 | 4.7409 | 4.5863 | 4.4227 | 4.2475 | 4.058 | 3.8504 | 3.621 | 3.3668 | 3.0881 | 2.7948
6 | 5.1222 | 4.9647 | 4.7993 | 4.624 | 4.4365 | 4.2335 | 4.0112 | 3.7656 | 3.4934 | 3.1949 | 2.8809
8 | 5.3788 | 5.2096 | 5.0318 | 4.8435 | 4.6421 | 4.424 | 4.1852 | 3.9213 | 3.6289 | 3.3083 | 2.9709
10 | 5.6609 | 5.4784 | 5.2868 | 5.0837 | 4.8665 | 4.6314 | 4.3739 | 4.0894 | 3.7741 | 3.4284 | 3.0646
12 | 5.9724 | 5.7749 | 5.5674 | 5.3475 | 5.1124 | 4.8578 | 4.579 | 4.271 | 3.9296 | 3.5553 | 3.1614
14 | 6.3181 | 6.1033 | 5.8775 | 5.6384 | 5.3826 | 5.1056 | 4.8023 | 4.4672 | 4.0959 | 3.6887 | 3.2602
16 | 6.7038 | 6.4688 | 6.2218 | 5.9603 | 5.6804 | 5.3775 | 5.0457 | 4.6791 | 4.2729 | 3.8275 | 3.3588
18 | 7.1365 | 6.8777 | 6.6058 | 6.3178 | 6.0097 | 5.6761 | 5.3108 | 4.9072 | 4.46 | 3.9696 | 3.4535
20 | 7.6246 | 7.3375 | 7.0357 | 6.7161 | 6.3742 | 6.004 | 5.5987 | 5.1508 | 4.6545 | 4.1103 | 3.5376
States
| Tsource | Tdrain | pCond | pA | hA | hB | hC | hD | sB | Work | qEvap | qOut | Yield | COP | YieldNormed
0 | 0 | 30 | 11000000 | 3485140.7577 | 268214.3906 | 430893.3407 | 477699.7094 | 268214.3906 | 1361.8072 | 4570517.2542 | 15885166.2338 | 20455683.4881 | 20455683.4881 | 4.4756 | 1.1035
1 | 0 | 32 | 11000000 | 3485140.7577 | 274267.503 | 430893.3407 | 477699.7094 | 274267.503 | 1361.8072 | 4570517.2542 | 15294095.9296 | 19864613.1838 | 19864613.1838 | 4.3463 | 1.0716
2 | 0 | 34 | 11000000 | 3485140.7577 | 280628.5343 | 430893.3407 | 477699.7094 | 280628.5343 | 1361.8072 | 4570517.2542 | 14672958.1638 | 19243475.418 | 19243475.418 | 4.2103 | 1.0381
3 | 0 | 36 | 11000000 | 3485140.7577 | 287365.9325 | 430893.3407 | 477699.7094 | 287365.9325 | 1361.8072 | 4570517.2542 | 14015069.1736 | 18585586.4278 | 18585586.4278 | 4.0664 | 1.0026
4 | 0 | 38 | 11000000 | 3485140.7577 | 294573.8849 | 430893.3407 | 477699.7094 | 294573.8849 | 1361.8072 | 4570517.2542 | 13311231.8108 | 17881749.065 | 17881749.065 | 3.9124 | 0.96465
5 | 0 | 40 | 11000000 | 3485140.7577 | 302376.711 | 430893.3407 | 477699.7094 | 302376.711 | 1361.8072 | 4570517.2542 | 12549306.6284 | 17119823.8826 | 17119823.8826 | 3.7457 | 0.92355
6 | 0 | 42 | 11000000 | 3485140.7577 | 310922.4738 | 430893.3407 | 477699.7094 | 310922.4738 | 1361.8072 | 4570517.2542 | 11714835.6453 | 16285352.8995 | 16285352.8995 | 3.5631 | 0.87853
7 | 0 | 44 | 11000000 | 3485140.7577 | 320363.0516 | 430893.3407 | 477699.7094 | 320363.0516 | 1361.8072 | 4570517.2542 | 10792988.3623 | 15363505.6165 | 15363505.6165 | 3.3614 | 0.8288
8 | 0 | 46 | 11000000 | 3485140.7577 | 330825.6317 | 430893.3407 | 477699.7094 | 330825.6317 | 1361.8072 | 4570517.2542 | 9771345.2864 | 14341862.5406 | 14341862.5406 | 3.1379 | 0.77369
9 | 0 | 48 | 11000000 | 3485140.7577 | 342298.084 | 430893.3407 | 477699.7094 | 342298.084 | 1361.8072 | 4570517.2542 | 8651090.8736 | 13221608.1278 | 13221608.1278 | 2.8928 | 0.71326
10 | 0 | 50 | 11000000 | 3485140.7577 | 354370.7232 | 430893.3407 | 477699.7094 | 354370.7232 | 1361.8072 | 4570517.2542 | 7472229.8046 | 12042747.0588 | 12042747.0588 | 2.6349 | 0.64966
11 | 2 | 30 | 11000000 | 3673285.9002 | 268214.3906 | 429652.6499 | 473603.6435 | 268214.3906 | 1350.4741 | 4574171.6273 | 16801583.8756 | 21375755.5029 | 21375755.5029 | 4.6731 | 1.1531
12 | 2 | 32 | 11000000 | 3673285.9002 | 274267.503 | 429652.6499 | 473603.6435 | 274267.503 | 1350.4741 | 4574171.6273 | 16171610.0643 | 20745781.6916 | 20745781.6916 | 4.5354 | 1.1192
13 | 2 | 34 | 11000000 | 3673285.9002 | 280628.5343 | 429652.6499 | 473603.6435 | 280628.5343 | 1350.4741 | 4574171.6273 | 15509589.7888 | 20083761.4162 | 20083761.4162 | 4.3907 | 1.0834
14 | 2 | 36 | 11000000 | 3673285.9002 | 287365.9325 | 429652.6499 | 473603.6435 | 287365.9325 | 1350.4741 | 4574171.6273 | 14808399.3694 | 19382570.9967 | 19382570.9967 | 4.2374 | 1.0456

## YieldComparison
Dette ark sammenligner for hvert kølemiddel (samme maskine) ydelsen sat i forhold til ydelsen per slugeevne ved referencetilstanden markeret med sort kant i tabellerne herunder.
| Tsource | Tdrain | NH3 at Tcond=60°C | NH3 at Tcond=70°C | NH3 at Tcond=80°C | NH3 at Tcond=90°C |  | Tsource | Tdrain | CO2 at pCond=90 bar | CO2 at pCond=100 bar | CO2 at pCond=110 bar | CO2 at pCond=120 bar
0 | 0 | 30 | 0.88625 | 0.91438 | 0.94215 | 0.96957 | 0 | 0 | 30 | 1.1117 | 1.1663 | 1.2116 | 1.2509
1 | 0 | 32 | 0.88014 | 0.90827 | 0.93606 | 0.96349 | 1 | 0 | 32 | 1.0652 | 1.1274 | 1.1766 | 1.2184
2 | 0 | 34 | 0.87399 | 0.90214 | 0.92994 | 0.9574 | 2 | 0 | 34 | 1.0114 | 1.0853 | 1.1398 | 1.1847
3 | 0 | 36 | 0.86782 | 0.89599 | 0.92381 | 0.95128 | 3 | 0 | 36 | 0.94503 | 1.0391 | 1.1008 | 1.1497
4 | 0 | 38 | 0.86163 | 0.88981 | 0.91764 | 0.94513 | 4 | 0 | 38 | 0.85455 | 0.98706 | 1.0591 | 1.113
5 | 0 | 40 | 0.8554 | 0.8836 | 0.91145 | 0.93896 | 5 | 0 | 40 | 0.72153 | 0.92676 | 1.014 | 1.0745
6 | 0 | 42 | 0.84914 | 0.87736 | 0.90523 | 0.93276 | 6 | 0 | 42 | 0.58459 | 0.85505 | 0.96456 | 1.0336
7 | 0 | 44 | 0.84285 | 0.87108 | 0.89898 | 0.92653 | 7 | 0 | 44 | 0.48797 | 0.76952 | 0.90996 | 0.99014
8 | 0 | 46 | 0.83653 | 0.86478 | 0.89269 | 0.92027 | 8 | 0 | 46 | 0.41802 | 0.67669 | 0.84945 | 0.94368
9 | 0 | 48 | 0.83017 | 0.85844 | 0.88637 | 0.91398 | 9 | 0 | 48 | 0.36276 | 0.58977 | 0.7831 | 0.89403
10 | 0 | 50 | 0.82377 | 0.85206 | 0.88002 | 0.90766 | 10 | 0 | 50 | 0.31651 | 0.51596 | 0.71328 | 0.84112
11 | 2 | 30 | 0.94366 | 0.97344 | 1.0029 | 1.0319 | 11 | 2 | 30 | 1.1608 | 1.2184 | 1.2661 | 1.3074
12 | 2 | 32 | 0.9371 | 0.9669 | 0.99632 | 1.0254 | 12 | 2 | 32 | 1.1112 | 1.1769 | 1.2287 | 1.2728
13 | 2 | 34 | 0.93051 | 0.96032 | 0.98976 | 1.0188 | 13 | 2 | 34 | 1.0539 | 1.1321 | 1.1895 | 1.2369
14 | 2 | 36 | 0.92389 | 0.95372 | 0.98318 | 1.0123 | 14 | 2 | 36 | 0.98316 | 1.0828 | 1.148 | 1.1996
15 | 2 | 38 | 0.91724 | 0.94708 | 0.97656 | 1.0057 | 15 | 2 | 38 | 0.88673 | 1.0273 | 1.1036 | 1.1605
16 | 2 | 40 | 0.91056 | 0.94042 | 0.96992 | 0.99906 | 16 | 2 | 40 | 0.74495 | 0.96307 | 1.0555 | 1.1194
17 | 2 | 42 | 0.90384 | 0.93372 | 0.96324 | 0.99241 | 17 | 2 | 42 | 0.59899 | 0.88664 | 1.0028 | 1.0759
18 | 2 | 44 | 0.89709 | 0.92699 | 0.95654 | 0.98573 | 18 | 2 | 44 | 0.49601 | 0.79549 | 0.94461 | 1.0295
19 | 2 | 46 | 0.89031 | 0.92023 | 0.94979 | 0.97901 | 19 | 2 | 46 | 0.42146 | 0.69654 | 0.88011 | 0.98003
20 | 2 | 48 | 0.88348 | 0.91342 | 0.94301 | 0.97226 | 20 | 2 | 48 | 0.36257 | 0.6039 | 0.80939 | 0.9271
21 | 2 | 50 | 0.87661 | 0.90658 | 0.9362 | 0.96547 | 21 | 2 | 50 | 0.31327 | 0.52524 | 0.73498 | 0.87071
22 | 4 | 30 | 1.0039 | 1.0354 | 1.0665 | 1.0972 | 22 | 4 | 30 | 1.2115 | 1.2723 | 1.3225 | 1.366
23 | 4 | 32 | 0.99685 | 1.0284 | 1.0595 | 1.0903 | 23 | 4 | 32 | 1.1586 | 1.228 | 1.2827 | 1.3291
24 | 4 | 34 | 0.98978 | 1.0213 | 1.0525 | 1.0833 | 24 | 4 | 34 | 1.0975 | 1.1802 | 1.2409 | 1.2909
25 | 4 | 36 | 0.98269 | 1.0143 | 1.0454 | 1.0762 | 25 | 4 | 36 | 1.0221 | 1.1277 | 1.1966 | 1.251
26 | 4 | 38 | 0.97556 | 1.0071 | 1.0383 | 1.0692 | 26 | 4 | 38 | 0.91926 | 1.0685 | 1.1492 | 1.2094
27 | 4 | 40 | 0.9684 | 1 | 1.0312 | 1.0621 | 27 | 4 | 40 | 0.76808 | 1 | 1.0979 | 1.1655
28 | 4 | 42 | 0.96121 | 0.99282 | 1.0241 | 1.0549 | 28 | 4 | 42 | 0.61245 | 0.9185 | 1.0418 | 1.1191
29 | 4 | 44 | 0.95397 | 0.98561 | 1.0169 | 1.0478 | 29 | 4 | 44 | 0.50264 | 0.8213 | 0.9797 | 1.0697
30 | 4 | 46 | 0.9467 | 0.97836 | 1.0096 | 1.0406 | 30 | 4 | 46 | 0.42314 | 0.7158 | 0.91093 | 1.0169
31 | 4 | 48 | 0.93938 | 0.97106 | 1.0024 | 1.0333 | 31 | 4 | 48 | 0.36035 | 0.61701 | 0.83552 | 0.96047
32 | 4 | 50 | 0.93202 | 0.96373 | 0.99507 | 1.0261 | 32 | 4 | 50 | 0.30778 | 0.53314 | 0.75617 | 0.90034
33 | 6 | 30 | 1.067 | 1.1003 | 1.1332 | 1.1657 | 33 | 6 | 30 | 1.2639 | 1.328 | 1.3809 | 1.4267
34 | 6 | 32 | 1.0595 | 1.0928 | 1.1257 | 1.1582 | 34 | 6 | 32 | 1.2074 | 1.2807 | 1.3384 | 1.3873